### TOWN OF NEW TECUMSETH

#### ANNUAL REPORT 2001

Location:	Tottenham Reservoir – Treated

| Microbiological Parameters | MAC or IMAC | Number Of Samples Taken | Number of Detectable Results | Sampling Date | Range | Exceedence? | Typical Source Of Contaminant |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Total Coliforms (counts/100ml) | 1 | 438 | 1 | 01/01/01- 12/31/01 | 0-25 | YES | Indicates possible presence of Fecal Matter |
| E-Coli (counts/100 ml) | 1 | 438 | 0 | 01/01/01- 12/31/01 | 0 | NO | Definite Indicator of Fecal Contamination |
| Background | 200 | 438 | 15 | 01/01/01- 12/31/01 | 0->2500 | YES | Indicator of Deteriorating Water Quality |
| Heterotrophic Plate Count (HPC) | 500 | 149 | 0 | 01/01/01- 12/31/01 | 0-464 | NO | Indicator of Deteriorating Water Quality |
| * Indicator of adverse water quality if detected in treated water |
| Parameters related to Microbiological Quality | MAC or IMAC | Number of Samples Taken | Number of Detectable Results | Sampling Date | Range | Exceedence? | Typical Source Of Contaminant |
| Turbidity (NTU) | 1 NTU | 151 | 151 | 01/01/01- 12/31/01 | 0-1 | NO | Indicates presence of dirt particles |
| Turbidity – Reservoir (NTU) | 1 NTU | Cont. 24 hr on-line samples | Continuous | 01/01/01- 12/31/01 | 0-1 | NO | Indicates presence of dirt particles |
| Fluoride |  | 47 | 47 | 01/01/01- 12/31/01 | .08-.50 | NO |  |
| Fluoride |  | Cont. 24 hr on-line monitoring | Continuous | 01/01/01- 12/31/01 |  | NO |  |
| Free Chlorine - Plant (mg/l) | N/A | Cont. 24 hr on-line monitoring | Continuous | 01/01/01- 12/31/01 | 0-4 | NO | Recommended Level 0.2 mg/L |
| Free Chlorine – System (mg/l) | N/A | 426 | 421 | 01/01/01- 12/31/01 | 0-1.84 | NO | Recommended Level 0.2 mg/L |
| Physical & Chemical | MAC or IMAC | Number of Samples Taken | Number of Detectable Results | Sampling Date | Range | Exceedence? | Typical Source Of Contaminant |
| Alkalinity | 30-500 mg/l | 3 | 3 | 01/01/01- 12/31/01 | 222-267 | NO | Calcium Chloride |
| Calcium |  | 3 | 0 | 01/01/01- 12/31/01 | 29-42 | N/A |  |
| Colour | 5 TCU | 3 | 0 | 01/01/01- 12/31/01 | 3 | NO | Natural Iron Manganese |
| Conductivity |  | 3 | 0 | 01/01/01- 12/31/01 | 522-531 | N/A |  |
| Hardness | 80-100 mg/l | 3 | 0 | 01/01/01- 12/31/01 | 184-195 | NO | Dissolved Calcium & Magnesium |

| PH | 6.5-8.5 | 3 | 0 | 01/01/01- 12/31/01 | 8.05-8.13 | NO | Acid or Base |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Temperature |  | 3 | 0 | 01/01/01- 12/31/01 | 10.5-12.7 | N/A |  |
| Total Kjeldahl Nitrogen | 0.15 mg/l | 3 | 0 | 01/01/01- 12/31/01 | 0.5-0.9 | NO |  |
| DOC | 5 mg/l | 3 | 0 | 01/01/01- 12/31/01 | 1.3-1.9 | NO | Growth Nutrient for Bacti |
| Inorganic Parameters | MAC or IMAC ((g/l) | Number of Samples | Number of Detectable Results | Sampling Date | Range | Exceedence? | Typical Source Of Contaminant |
| Aluminium |  | 0 | 0 | 01/01/01- 12/31/01 |  |  |  |
| Ammonia-N + Ammonium-N |  | 0 | 0 | 01/01/01- 12/31/01 |  |  |  |
| Arsenic | 25 | 1 | 0 | 01/01/01- 12/31/01 | 2 | NO | Known carcinogen |
| Barium | 1000 | 1 | 0 | 01/01/01- 12/31/01 | 36 | NO | Constituent of rock |
| Boron | 5000 | 1 | 0 | 01/01/01- 12/31/01 | 27 | NO | Antiseptic Agent |
| Cadmium | 5 | 1 | 0 | 01/01/01- 12/31/01 | 0.1 | NO | Used in Electroplating |
| Chloride |  | 0 | 0 | 01/01/01- 12/31/01 |  |  |  |
| Chromium | 50 | 1 | 0 | 01/01/01- 12/31/01 | 3 | NO | Not considered toxic |
| Copper | 1000 | 1 | 0 | 01/01/01- 12/31/01 | 64 | NO | Plumbing material |
| Cyanide |  | 0 | 0 | 01/01/01- 12/31/01 |  |  |  |
| Fluoride |  | 47 | 47 | 01/01/01- 12/31/01 | .08-.50 | NO |  |
| Iron | 300 | 2 | 1 | 01/01/01- 12/31/01 | 758 | YES | Mineral deposit |
| Lead | 10 | 1 | 0 | 01/01/01- 12/31/01 | 0.6 | NO | Plumbing material |
| Manganese | 50 | 1 | 0 | 01/01/01- 12/31/01 | 0.3 | NO | Stains plumbing fixtures |
| Mercury | 1 | 1 | 0 | 01/01/01- 12/31/01 | 0.1 | NO | Coal combustion |
| Nitrate+Nitrite (as N) | 10 mg/l | 4 | 0 | 01/01/01- 12/31/01 | 0.021-0.032 | NO |  |
| Nitrate | 10 mg/l | 4 | 0 | 01/01/01- 12/31/01 | 0.021-0.032 | NO | Plant & animal decay |
| Nitrite | 1 mg/l | 4 | 0 | 01/01/01- 12/31/01 | 0.011 | NO | Blue babies |
| Phenols |  | 0 | 0 | 01/01/01- 12/31/01 |  |  |  |

| Selenium | 10 | 1 | 1 | 01/01/01- 12/31/01 | 3 | NO | Geochemical process |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sodium |  | 2 | 2 | 01/01/01- 12/31/01 | 10.4-48.6 | NO |  |
| Sulphate |  | 0 | 0 | 01/01/01- 12/31/01 |  |  |  |
| Total dissolved solids |  | 0 | 0 | 01/01/01- 12/31/01 |  |  |  |
| Uranium | 100 | 1 | 1 | 01/01/01- 12/31/01 | 0.05 | NO | Can damage kidneys |
| Zinc |  | 0 | 0 | 01/01/01- 12/31/01 |  |  |  |
| Volatile Organics | MAC or IMAC ((g/l) | Number of Samples Taken | Number of Detectable Results | Sampling Date | Range | Exceedence? | Typical Source Of Contaminant |
| Benzene | 5 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.36 | NO | Petroleum by-product |
| Carbon Tetrachloride | 5 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.34 | NO | Solvent |
| 1,2-Dichlorobenzene | 200 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.56 | NO | Degreaser agent |
| 1,4-Dichlorobenzene | 5 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.25 | NO | Used for moth balls |
| 1,2-Dichloroethane | 5 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.56 | NO | Solvent |
| 1,1-Dichloroethylene | 14 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.52 | NO |  |
| Dichloromethane | 50 | 4 | 4 | 01/01/01- 12/31/01 | 0-1.17 | NO | Solvent |
| Ethylbenzene | 2.4 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.47 | NO | Solvent for paint base |
| Monochlorobenzene | 80 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.46 | NO | Solvent for adhesives |
| Tetrachloroethylene | 30 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.48 | NO | Solvent for dry cleaning |
| Toluene | 24 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.58 | NO | Petroleum by-product, metal degreaser |
| Total Trihalomethanes | 100 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.49 | NO | Chlorine by-product |
| Trichloroethylene | 50 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.54 | NO |  |
| Vinyl chloride | 2 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.08 | NO | Common plastics |
| Xylene | 300 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.58 | NO | Industrial solvent |
| Pesticides and PCB’s | MAC or IMAC ((g/l) | Number of Samples Taken | Number of Detectable Results | Sampling Date | Range | Exceedence? | Typical Source Of Contaminant |
| Alachlor | 5 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.40 | NO | Herbicide |
| Aldicarb | 9 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.56 | NO | Insecticide |
| Aldrin+Dieldrin | 0.7 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.50 | NO | Insecticide |
| Atrazine | 5 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.43 | NO | Herbicide |
| Azinphos-methyl | 20 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.59 | NO | Insecticide |
| Bendiocarb | 40 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.27 | NO | Insecticide |
| Bromoxynil | 5 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.60 | NO | Herbicide |
| Carbaryl | 90 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.14 | NO | Insecticide |
| Carbofuran | 90 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.14 | NO | Insecticide |
| Chlordane (Total) | 7 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.20 | NO | Insecticide |
| Chlorpyrifos | 90 | 4 | 4 | 01/01/01- 12/31/01 | 0-1.20 | NO | Herbicide |
| Cyanazine | 10 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.79 | NO | Insecticide |
| Diazinon | 20 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.41 | NO | Insecticide |
| Dicamba | 120 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.90 | NO | Herbicide |
| DDT | 30 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.46 | NO | Insecticide |
| 2,4-D | 100 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.33 | NO | Herbicide |
| 2,4-Dichlorophenol | 900 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.14 | NO |  |
| Diclofop-methyl | 9 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.84 | NO | Insecticide |
| Dimethoate | 20 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.10 | NO | Insecticide |
| Dinoseb | 10 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.42 | NO | Insecticide |
| Diquat | 70 | 4 | 4 | 01/01/01- 12/31/01 | 0-1.0 | NO | Herbicide |
| Diuron | 10 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.66 | NO | Herbicide |
| Glyphosate | 280 | 4 | 4 | 01/01/01- 12/31/01 | 0-6.0 | NO | Herbicide |
| Heptachlor + Heptachlor epoxide | 3 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.20 | NO |  |
| Lindane (Total) | 4 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.13 | NO | Insecticide |
| Malathion | 190 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.37 | NO | Insecticide |

| Methoxychlor | 900 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.64 | NO | Insecticide |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Metolachlor | 50 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.58 | NO | Insecticide |
| Metribuzin | 80 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.50 | NO | Herbicide |
| Paraquat | 10 | 4 | 4 | 01/01/01- 12/31/01 | 0-1.0 | NO | Herbicide |
| Parathion | 50 | 4 | 4 | 01/01/01- 12/31/01 | 0-1.20 | NO |  |
| Pentachlorophenol | 60 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.31 | NO |  |
| Phorate | 2 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.73 | NO | Insecticide |
| Picloram | 190 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.19 | NO | Insecticide |
| PCB | 3 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.04 | NO | Organic Pollutant |
| Prometryne | 1 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.16 | NO | Herbicide |
| Simazine | 10 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.18 | NO | Herbicide |
| Temephos | 280 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.25 | NO | Insecticide |
| Terbufos | 1 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.73 | NO | Insecticide |
| 2,3,4,6-Tetrachlorophenol | 100 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.20 | NO | Organic Pollutant |
| Triallate | 230 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.14 | NO | Herbicide |
| 2,4,6-Trichlorophenol | 5 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.20 | NO | Organic Pollutant |
| Trifluralin | 45 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.35 | NO | Herbicide |
| 2,4,5-T Trichlorophenoxyacetic Acid | 280 | 4 | 4 | 01/01/01- 12/31/01 | 0-0.47 | NO | Organic Pollutant |
| * THM MAC is based on a running annual average of four quarterly samples. This value is the average of the most recent four detects. |